DIVISION 8

SECTION 08300

SPECIALTY DOOR SYSTEMS

PART 1 - GENERAL

1.01	SECTION INCLUDES

A.	Fabric Roll-Up doors and accessories for complete installation.

1.02	RELATED SECTIONS

A.	Division 16 – Electrical.

1.03	SUBMITTALS

A.	Product Data: Completely describing components.

B.	Shop Drawings: Showing details of fabrication, installation and accommodation to connecting work.

C.	Installation Instructions: For door, operator and accessories.

- Operating and Maintenance Data: For door, operator and accessories.

1.04	QUALITY ASSURANCE

A.	Installer Qualification: Door manufacturer, or trained, approved and licensed door installer.

PART 2 - PRODUCT

2.01	MANUFACTURERS

- Model 615F Insulated Fabric Roll-Up Door System by ASI Doors, Inc., Milwaukee, WI.

B.	Substitutions:

No substitution will be considered unless written request for approval has been submitted by the bidder and has been received by the architect at least ten (10) days prior to the date for receipt of bids.

Each such request shall include the name of the materials for which it is to be substituted and a complete description of the proposed substitute, including drawings, cuts, mockups, performance and test data, a list of projects of similar scope and photographs of existing installations, and any other information necessary for evaluation.

2.02	FABRIC ROLL-UP DOORS

A.	Model 615F High Speed Insulated Fabric Roll-Up Door System.

- Door size to fit door opening _____ wide X _____ high or shown on architectural drawings.

- Doors shall be high speed electric powered fabric roll-up doors.

- Fabric to be a polyester multifilament PVC coated curtain material. Panel color to be a standard blue or orange. (Optional colors available.)

a)	Optional fabric consisting of two standard layers of PVC, filled with insulating material can be specified to reduce convection.

- Electric operator to allow for opening speeds of up to 100 inches per second. Electric motor to be 2 hp, 230/460 volts, 3 phase unit. Two speed operation 100"/sec. open, 50"/sec. close. Self-diagnostic custom microprocessor with variable frequency motor drive allows for speed to be fully adjustable.

- Electric control panel to be in a NEMA-4 rated enclosure, assembled and ready for connection by others. Control panel must have push button emergency stop.

- Curtain bottom edge to be free of any rigid structural pieces or reversing device components. Curtain reversing during door travel to be provided through an advanced sensing system located in the side guides of the door. Fabric door will reverse during downward travel when pressure is applied to the bottom of the curtain. Reversing edge components, transmitters, batteries, wires in or on the bottom edge or sides of curtain will not be allowed; coil cords are also not allowed.

- Send and receive photo eye to be provided.

- Absolute encoder to provide infinite adjustment. Adjustments to be made without the aid of special tools. NO DOOR TRAVEL SETTINGS NEED TO BE RESET AFTER POWER LOSS. Doors requiring manual assistance, recalibration, or operator interface with door controls after power loss are not allowed.

9.	Door actuation to be provided by:

a)	Single control with Open / Close and Emergency Stop push buttons.

or options:

b)	Ceiling mounted, low voltage pull switch.

or

c)	Radio control actuator

or

d)	Motion detector system

10.	Curtain displacement and recapture system:

a)	Door curtain shall be able to release at any point of the full height on both edges of door.

b)	 Door curtains that partially release are not acceptable.

c)	Impacted or displaced curtain will automatically recapture itself on the next upward cycle. Doors requiring manual assistance, recalibration, or operator interface with door controls for curtain alignment are not allowed.

d)	Doors requiring breakable tabs, tape connections, or wind knobs or wheels on the curtain will not be allowed.

- Springs in barrels and/or side columns will not be allowed. Tension straps will not be allowed.

- Curtain & Track Retention System

a)	Door curtain to be free of any rigid profiles, structural stiffeners and bottom bars.

b)	Door curtain top seal integrated to door curtain. Top seal rolls up with door to prevent scraping of vision window and curtain discoloration. Seal to automatically deploy against wall when door is fully closed. Door curtains with top seal penetrating wall or constant contact while door rolls up are not allowed.

c)	Top to bottom continuous side seals. Curtain edges to have continuous lateral reinforced strips from floor to top of opening eliminating potential of gaps for air infiltration. Doors using brush seals or gasket seals which touch fabric as the door rolls are not acceptable.

d)	Continuous track system to fully retain curtain the entire length of the side guides and require no more than ½” gap for door curtain edges to travel inside of. Track Systems requiring additional brushes or gasket attached to side frames are not acceptable.

e)	Integrated heated side guides and lintel seal. Doors without side guide and lintel heat will not be allowed.

f)	Side guides to be provided with polyethylene thermal breaks.

g)	Low profile side column requires 5-1/2” wall space on each side of door opening.

13.	Provide a minimum 16-gauge galvanized steel side guide/frame system. (Optional stainless steel.)

14.	Optional non-heated and heated air circulation systems.

PART 3 - EXECUTION

3.01	EXAMINATION

- Verify installation conditions as satisfactory to receive work of this section. Do not install until unsatisfactory conditions are corrected. Beginning work constitutes your acceptance of conditions as satisfactory.

- Verify opening size, dimensions and tolerances.

3.02	PREPARATION

A.	Protect surrounding areas and surfaces to prevent damage during work of this section.

3.03	INSTALLATION

A.	Install the work in accordance with manufacturer instructions.

3.04	WARRANTIES

A.	One-year limited warranty on all components.

3.05	CLEANING

A.	Leave the premises clean and free of residue of work of this section.

END OF SECTION