DIVISION 8

SECTION 08300

COLD STORAGE DOOR SYSTEMS

PART 1- GENERAL

1.01 SECTION INCLUDES

A. IXP Impactable Bi-Parting Horizontal Sliding doors and accessories for complete installation.

1.02 RELATED SECTIONS

A.	Division 16 – Electrical

1.03 SUBMITTALS

A.	Product Data: Completely describing components.

B.	Shop Drawings: Showing details of fabrication, installation and accommodation to connecting work.

C.	Installation Instructions: For door, operator and accessories.

D. 	Operating and Maintenance Data: For door, operator and accessories.

1.04 QUALITY ASSURANCE

A.	Installer Qualification: Door manufacturer, or trained, approved and licensed door installer.

PART 2 - PRODUCT

2.01 MANUFACTURERS

A.	Model IXP 2100 Impactable Bi-Parting Horizontal Sliding Door as manufactured ASI Doors, Inc., Milwaukee, WI.

B. 	Substitutions:

No substitution will be considered unless written request for approval has been submitted by the bidder and has been received by the architect at least ten (10) days prior to the date for receipt of bids.

Each such request shall include the name of the materials for which it is to be substituted and a complete description of the proposed substitute, including drawings, cuts, mockups, performance and test data, a list of projects of similar scope and photographs of existing installations, and any other information necessary for evaluation.

2.02 GALVANIZED STEEL BI-PARTING HORIZONTAL SLIDING DOORS

A.	Model IXP 2100 Impactable Bi-Parting Horizontal Sliding Door.

1.	Door size to fit door opening as shown on architectural drawings and to conform to APHIS-U.S.D.A. (M.I.D.) sanitation regulations.

2.	Door Operation:

2.1	Door shall be manual operated, white stucco-embossed galvanized Bi-parting Horizontal Sliding.

2.2 	Door shall be high dual speed electric operated, white stucco-embossed galvanized Bi-parting Horizontal Sliding.

a.	1 hp Electro-Mechanical High Dual Speed Operator - Door speeds up to 96” / sec. open; up to 48” / sec. close.

b.	AC motor with Clutch-less, brakeless operation.

c.	PLC (Programmable Logic Control)

d.	Encoded, self-calibrating limit position.

e.	H.M.I. (Human Machine Interface). Digital display with self-diagnostics and fault indicators.

f.	VFD – (variable frequency drive).

g.	Torque sensing stop/reverse for height of door panels.

h.	High tensile strength reinforced polyurethane drive belt.

3.	Door panels shall consist of white stucco-embossed galvanized steel skin, filled with poured polyurethane insulation and bonded into a fully unitized panel.

4.	Standard door construction including panels, frames and header to be free of any wood construction. (Note: Door utilizing any wood construction will not be accepted).

5.	Panels to be reinforced with 12 gauge galvanized steel “C” channel plates at top of doors.

6.	4” panels to be unitized and fully insulated. Panels to meet a minimum insulation rating of R-32. (Note: Doors must meet minimum R-Value. Panels surfaced with fabric or utilizing moisture absorbent foam will not be accepted.)

7.	Door system to have breakaway panels with full impact capability up to a 90° angle in both directions. Leading edge breakaway panels to be a minimum of 18” in width and designed to allow for a bi-directional swing capability in either direction. Leading edge breakaway panels to be sized to allow swing capability into openings without impacting door headers. Breakaway door panels to be reinforced with 48” high 1/8” thick HDPE impact plating on both sides of panels. (Note: doors without full 90° swing capability in both directions will not be accepted.)

8.	Panels to have an automatic cutout switch built into header to cut off power to door in the event of an impact. Power to be automatically restored upon leading edge panel realignment.

9.	Standard header to be aluminum extrusion. (Note: Metal wrapped wood will not be accepted.)

10.	Standard rail to be self-cleaning, one piece aluminum extrusion.

11.	Standard track system to be angled to provide “down” panel movement when closing.

12.	Standard face frames to be one piece aluminum extrusion (with built-in races for self regulating heater wire on freezer doors). Face frames to be fitted with adjustable high-density polypropylene, grease resistant, moisture-proof cover. (Note: Steel wrapped wood face frames will not be accepted).

13.	Sill gasket to be double urethane sweep type.  Full height EPDM rubber at the trail edge of each panel for panel to frame seal.

14.	Single piece roller trucks, trolleys and hardware to be heavy duty, galvanized steel. Complete rail and truck hardware to be factory mounted on header.

15.	Trolley wheels to be nylon with dual lubed for life ball bearing systems, allowing for smooth, quiet high-speed door operation. (Note: Doors utilizing steel roller wheels will not be accepted.)

16.	Panels to be guided during travel by wall mounted track system. Track system to release door panels in the event of impact through a flexible spring steel latching tab. Latching tab connects to door panels through a fully adjustable bracket. Door panels when impacted will automatically return to track system once door panels go to full open position. (Note: Doors requiring floor-mounted hardware, retention straps or manual panel retention hardware resets, will not be accepted.)

17.	Power drive system to be electric operated belt driven, providing smooth high-speed operation. Includes automatic limit positioning through motor shaft mounted encoder. Manual operation in the event of a power failure. Electric motor to be 1 hp, 208/230/460 volt, three phase power required. (Note: Doors utilizing chain drives, separate limit switch devices will not be accepted.)

18.	Electrical controls to be enclosed in a NEMA-4 fiberglass control box. Electric controls must include a programmable logic controller and variable frequency drive system. (Note: Door systems without programmable logic control will not be accepted.)

19.	Instant panel reversing capability through monitoring of amp draw of motor. (Note: Doors utilizing electric or pneumatic reversing edges will not be allowed.)

20.	Door actuation to be provided by:

a.	Two single control push buttons, or ceiling mounted, low voltage pull cord switches included. Two Falcon motion sensors included.

or options:

b.	Radio control actuator.

c.	Motion or presence detector systems.

d.	Loop detector.

e.	Pre Announce to Close Kit (Light / Alarm / Combo).

[Note: Standard time delay close operation included.]

21.	Freezer doors to be equipped with an integrated fully protected self-regulating heat system utilizing UL recognized components. (Note: Doors utilizing heated blowers, fans or infrared heat of any kind will not be accepted).

22.	Center door panel gaskets to be full door height and offsetting to provide a tight effective seal.

23. 	Bare white HDPE mirror image header same width and height of head rail assembly.

24. 	Bare white HDPE inside trim to mirror the face frames.

25. 	White HPDE 36” kick plates on both sides of fix door panel.

26.	Complete rail, truck and operator assembly to be mounted and tested at factory.

27.	Complete system to be assembled and ready for installation (by others).

28.	Operating Temperatures: Door mounted in applications below 33°F, consult factory for heated motor, controls and low temp encoder package.

PART 3 - EXECUTION

3.01 EXAMINATION

A.	Verify installation conditions as satisfactory to receive work of this section. Do not install until unsatisfactory conditions are corrected. Beginning work constitutes your acceptance of conditions as satisfactory.

1.	Verify opening size, dimensions and tolerances.

3.02 PREPARATION

A.	Protect surrounding areas and surfaces to prevent damage during work of this section.

3.03 INSTALLATION

A.	Mechanically install the work in accordance with manufacturer instructions.

B.	All electrical high power and low voltage wiring to be supplied, installed and connections to doors are to be by electrical contractor.

C.	Wall construction (by others) to be sufficient to support the door assembly and to support the operation of the door panel.

3.04 WARRANTIES

A.	One year limited warranty on all components.

3.05 CLEANING

A.	Leave the premises clean and free of residue of work of this section.

END OF SECTION