# DIVISION 8

SECTION 08300

### SPECIALTY DOOR SYSTEMS

PART 1 – GENERAL

1.01 SECTION INCLUDES

- Single Sliding Seamless Molded Fiberglass Door System and accessories for complete installation.

  - RELATED SECTIONS

- Division 16 – Electrical.

  - SUBMITTALS

- Product Data: Completely describing components.

- Shop Drawings: Showing details of fabrication, installation and accommodation to connecting work.

- Installation Instructions: For door, operator and accessories.

- Operating and Maintenance Data: For door, operator and accessories.

  - QUALITY ASSURANCE

A.	Installer Qualification: Door manufacturer, or trained, approved and licensed door installer.

PART 2 - PRODUCT

2.01 MANUFACTURERS

A.	Model 1240 Excel Single Sliding Seamless Molded Fiberglass Door System as manufactured by Doors, Inc., Milwaukee, WI.

B.	Substitutions:

No substitution will be considered unless written request for approval has been submitted by the bidder and has been received by the architect at least ten (10) days prior to the date for receipt of bids.

Each such request shall include the name of the materials for which it is to be substituted and a complete description of the proposed substitute, including drawings, cuts, mockups, performance and test data, a list of projects of similar scope and photographs of existing installations, and any other information necessary for evaluation.

  - SINGLE PIECE HORIZONTAL SLIDING CLEANROOM DOORS

- Model 1240 Excel Single Sliding Seamless Molded Fiberglass Door System.

- Door size to fit door opening as shown on architectural drawings.

- Doors shall be manually operated, Single Sliding Seamless Molded Fiberglass Door System.

- Door panel shall consist of two molded fiberglass reinforced polyester shells surfaced with white (specify if other color is required) polyester gel-coat and bonded into a seamless unit. (Laminated/glued FRP, ABS or Kydex sheet will not be accepted.) Corners and edges to be reinforced to a thickness of 5/8". Panel to be reinforced with an internal 16 gauge channel steel frame with 1/4" steel attachment plates at top for attaching panel. Also, a 20 gauge, 304, #4 stainless steel edge capping will be attached on all four sides of panel for added strength and protection.

4.	1-3/4” thick panel to be unitized and filled with pour-type polyurethane foam insulation (rated at R-16) having a “K” factor of .12 at 75° F.

5.	Door shall be manually operated with an automatic closer and "hold-open" feature in the fully open position. The automatic closer system shall utilize a cable reel system with a shock absorber to eliminate bounce back and the door staying open. (Closer systems utilizing counterweights will not be accepted.)

- Rail, header and trolley assembly to be heavy-duty stainless steel construction. Trolley assembly to incorporate adjustments in both the vertical and horizontal planes for optimal sealing. Header and rail assemblies constructed or clad with aluminum or other soft metals will not be accepted. Entire header and rail assembly to be enclosed by a 16 gauge stainless steel shroud, with a sloped top.

- Provide a guide roller on the trailing edge base of the opening and the leading edge base of the opening, attached to an 11 gauge stainless steel plate mounted to the side frame. (Hardware attached to the floor will not be accepted.)  This will allow the panel to hold the optimal panel seal under both positive and negative pressures.

- Gasket at sides, head and sill to be gray vinyl, non-marking, blade type, capable of holding a seal under positive/negative pressures.

- Side frames to be two piece stainless steel construction, 16 gauge. When attached to the wall, bolt heads, nuts, or fastener covers will not be visible. (Frames requiring these items will not be accepted.)

- Hardware to include stainless steel recessed handles and stainless steel floor hardware. Truck wheels to be nylon with factory sealed ball bearings. Complete rail and trolley hardware to be stainless steel and mounted on a stainless steel header.

11.	Window kit option will include two 45 degree sloped stainless steel frames connected internally (no exposed fasteners) with ¼” thick tempered glass.

OR optional:

12.	Window kit option will include two sheets of 3/16” thick tempered glass bonded to an internal framework and installed in the door panel to create a flush window condition on both sides of the door panel.

PART 3 – EXECUTION

  - EXAMINATION

- Verify installation conditions as satisfactory to receive work of this section. Do not install until unsatisfactory conditions are corrected. Beginning work constitutes your acceptance of conditions as satisfactory.

- Verify opening size, dimensions and tolerances.

  - PREPARATION

- Protect surrounding areas and surfaces to prevent damage during work of this section.

  - INSTALLATION

- Install the work in accordance with manufacturer instructions.

  - WARRANTIES

- Two year limited warranty on all components.

  - CLEANING

A.	Leave the premises clean and free of residue of work of this section.

## END OF SECTION