# DIVISION 8

SECTION 08300

### SPECIALTY DOOR SYSTEMS

PART 1 – GENERAL

1.01 SECTION INCLUDES

- Bi-Part Sliding Fiberglass Door System and accessories for complete installation.

  - RELATED SECTIONS

- Division 16 – Electrical.

  - SUBMITTALS

- Product Data: Completely describing components.

- Shop Drawings: Showing details of fabrication, installation and accommodation to connecting work.

- Installation Instructions: For door, operator and accessories.

- Operating and Maintenance Data: For door, operator and accessories.

  - QUALITY ASSURANCE

A.	Installer Qualification: Door manufacturer, or trained, approved and licensed door installer.

PART 2 - PRODUCT

2.01 MANUFACTURERS

A.	Model 170 LXP Bi-Part Sliding Fiberglass Door System as manufactured by ASI Doors, Inc., Milwaukee, WI.

B.	Substitutions:

No substitution will be considered unless written request for approval has been submitted by the bidder and has been received by the architect at least ten (10) days prior to the date for receipt of bids.

Each such request shall include the name of the materials for which it is to be substituted and a complete description of the proposed substitute, including drawings, cuts, mockups, performance and test data, a list of projects of similar scope and photographs of existing installations, and any other information necessary for evaluation.

  - BI-PARTING DOUBLE HORIZONTAL SLIDING CLEANROOM DOORS

- Model 170 LXP Bi-Part Sliding Fiberglass Door System.

- Door size to fit door opening as shown on architectural drawings.

- Doors shall be manually operated, Bi-Part Sliding Fiberglass Door System.

- Door panels will be 1-3/4” thick and shall consist of two rigid white fiberglass reinforced polyester resin sheets surfaced with clear polyester gel-coat and bonded to an expanded polystyrene core having a “K” factor of .24 at 75º F.  Also, a 20 gauge stainless steel edge capping will be attached on all four sides of panel for added strength and protection.

- Header and rail assembly to be extruded and anodized aluminum construction.  Rail to be insulated from header by noise absorbing elastomer extrusion.   Truck assembly to incorporate adjustments in both the vertical and horizontal planes for optimal sealing.

- Entire header and rail assembly to be enclosed by a 16 gauge stainless steel shroud, with a sloped top.

- Provide a guide roller on the trailing edge base of the opening and the leading edge base of the opening, attached to an 11 gauge stainless steel plate mounted to the side frame. (Hardware attached to the floor will not be accepted.)  This will allow the panel to hold the optimal panel seal under both positive and negative pressures.

- Gasket at sides, head and sill to be gray vinyl, non-marking, non-shedding, non-absorptive blade type, capable of holding a seal under positive/negative pressures.

- Side frames to be two-piece stainless steel construction, 16 gauge. When attached to the wall, bolt heads, nuts, or fasteners will not be visible on the face of the side frames.  (Frames requiring these items will not be accepted.)

- Hardware to include stainless steel recessed pull handles and stainless steel floor hardware. Truck wheels to be nylon with factory sealed ball bearings.

- Window kit option will include two 45 degree sloped stainless steel frames connected internally (no exposed fasteners) with ¼” thick tempered glass.

PART 3 – EXECUTION

  - EXAMINATION

- Verify installation conditions as satisfactory to receive work of this section. Do not install until unsatisfactory conditions are corrected. Beginning work constitutes your acceptance of conditions as satisfactory.

- Verify opening size, dimensions and tolerances.

  - PREPARATION

- Protect surrounding areas and surfaces to prevent damage during work of this section.

  - INSTALLATION

- Install the work in accordance with manufacturer instructions.

  - WARRANTIES

- Two year limited warranty on all components.

  - CLEANING

A.	Leave the premises clean and free of residue of work of this section.

## END OF SECTION