# DIVISION 8

SECTION 08300

SPECIALTY DOOR SYSTEMS

PART 1 - GENERAL

1.01 SECTION INCLUDES

A.	Manual Single Swinging Seamless Molded Fiberglass Door System and accessories for complete installation.

1.02 RELATED SECTIONS

A.	Division 16 - Electrical.

1.03 SUBMITTALS

A.	Product Data: Completely describing components.

- Shop Drawings: Showing details of fabrication, installation and accommodation to connecting work.

- Installation Instructions: For door and accessories.

- Operating and Maintenance Data: For door and accessories.

1.04 QUALITY ASSURANCE

A.	Installer Qualification: Door manufacturer, or trained, approved and licensed door installer.

PART 2 - PRODUCT

2.01 MANUFACTURERS

A.	Model 220 Excel Single Swinging Seamless Molded Fiberglass Door System as manufactured by ASI Doors, Inc., Milwaukee, WI.

B.	Substitutions:

No substitution will be considered unless written request for approval has been submitted by the bidder and has been received by the architect at least ten (10) days prior to the date for receipt of bids.

Each such request shall include the name of the materials for which it is to be substituted and a complete description of the proposed substitute, including drawings, cuts, mockups, performance and test data, a list of projects of similar scope and photographs of existing installations, and any other information necessary for evaluation.

2.02 MANUAL SINGLE SWINGING CLEANROOM DOORS

A.	Model 220 Excel Single Swinging Seamless Molded Fiberglass Door System.

1.	Door size to fit door opening as shown on architectural drawings.

2.	Door shall be Manual Single Swinging Seamless Molded Fiberglass Cleanroom Door System.

3.	Door panel shall consist of two molded fiberglass reinforced polyester shells surfaced with white (specify if other color is required) polyester gel-coat and bonded into a seamless unit.  Corners and edges to be reinforced to a thickness of 5/8". Panel to be reinforced with an internal 16 gauge channel steel frame with 1/4" steel attachment plates for attaching panels.  Also, a 20 gauge 304 stainless steel edge capping will be attached on all four sides of panel for added strength and protection.

4.	1-3/4" thick panel to be unitized and filled with pour-type polyurethane foam insulation (rated at -R-16) having a “K” factor of .12 at 75 F.

5.	Frame shall be 16 gauge, 304 stainless steel with 2” face, mitered in the corners, welded, ground and polished, providing smooth, flush seamless surfaces.  Additionally the mitered corners must be continuously welded through the throat (rabbet(s) and stop) eliminating any seams or the appearance of seams.

- Standard hardware to include: stainless steel butt hinges, applied with stainless steel fasteners; and push / pull handles, constructed of stainless steel on exposed surfaces.

- Standard closer to manual open and spring close.  (Hardware to be manufacturers standard unless otherwise specified.)

8.	Gasket at sides, head and sill to be non-marking.

9.	Vision panel option will include two 45 degree sloped stainless steel frames connected internally with no exposed fasteners on either side of the door panel.  (Flush glass available as an option.)  Also include factory installed 1/4" tempered glass.

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Verify installation conditions as satisfactory to receive work of this section. Do not install until unsatisfactory conditions are corrected. Beginning work constitutes your acceptance of conditions as satisfactory.

1.	Verify opening size, dimensions and tolerances.

3.02 PREPARATION

A.	Protect surrounding areas and surfaces to prevent damage during work of this section.

3.03 INSTALLATION

A.	Install the work in accordance with manufacturer instructions.

3.04 WARRANTIES

A.	Two year limited warranty on all components.

3.05 CLEANING

A.	Leave the premises clean and free of residue of work of this section.

END OF SECTION