DIVISION 8

SECTION 08300

SPECIALTY DOOR SYSTEMS

PART 1 - GENERAL

1.01 SECTION INCLUDES

A.	Power operated Single Swinging Stainless Steel Door System and accessories for complete installation.

1.02	RELATED SECTIONS

A.	Division 16 - Electrical

1.03	SUBMITTALS

A.	Product Data: Completely describing components.

- Shop Drawings: Showing details of fabrication, installation and accommodation to connecting work.

- Installation Instructions: For door, and accessories.

- Operating and Maintenance Data: For door, and accessories.

1.04	QUALITY ASSURANCE

A.	Installer Qualification: Door manufacturer, or trained, approved and licensed door installer.

PART 2 - PRODUCT

2.01 MANUFACTURERS

A.	Model 225SS power operated Excel Single Swinging Stainless Steel Door System as manufactured by ASI Doors, Inc., Milwaukee, WI.

B.	Substitutions:

No substitution will be considered unless written request for approval has been submitted by the bidder and has been received by the architect at least ten (10) days prior to the date for receipt of bids.

Each such request shall include the name of the materials for which it is to be substituted and a complete description of the proposed substitute, including drawings, cuts, mockups, performance and test data, a list of projects of similar scope and photographs of existing installations, and any other information necessary for evaluation.

2.02	SINGLE SWINGING STAINLESS STEEL DOORS

A.	Model 225SS power operated Excel Single Swinging Stainless Steel Door System.

1.	Door size to fit door opening as shown on architectural drawings.

2.	Doors shall be electric power operated, Single Swinging Stainless Steel Door System.

3.	Door panel shall be made of 16 gauge type 304, #4 stainless steel.  Doors shall have INVISIBLE EDGE SEAMS continuously welded, ground smooth, refinished, and repolished on all four sides and corners of panel.  All hardware reinforcements to be minimum 12 gauge steel.  Door bevel shall be 1/8” bevel on 2”.

4.	Door shall have a styrene core laminated to both face skins.

5.	Frame shall be 16 gauge, 304 stainless steel with 2” face, mitered in the corners, welded, ground and polished, providing smooth, flush seamless surfaces.  Additionally the mitered corners must be continuously welded through the throat (rabbet(s) and stop) eliminating any seams or the appearance of seams.

6.	Standard hardware to include: stainless steel butt hinges, applied with stainless steel fasteners; and push / pull handles, constructed of stainless steel on exposed surfaces.

7.	Power drive system to be mechanically operated, 110 volt single phase power open and spring close.  Operator works as a conventional manual door closer in event of power failure.

8.	Door actuation to be provided by one or more of the following:

-	Two wall mounted push plates with time delay close.

-	Motion detector system.

-	Interlock system.

9.	Swing side of door to be protected by a head mounted active reflecting infrared motion sensor device.

10.	Gasket at sides, head and sill to be non-marking.

11.	Vision panel option will include two 45 degree sloped stainless steel frames connected internally with no exposed fasteners on either side of the door panel.  (Flush glass available as an option.)  Also include factory installed 1/4" tempered glass.

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Verify installation conditions as satisfactory to receive work of this section. Do not install until unsatisfactory conditions are corrected. Beginning work constitutes your acceptance of conditions as satisfactory.

1.	Verify opening size, dimensions and tolerances.

3.02	PREPARATION

A.	Protect surrounding areas and surfaces to prevent damage during work of this section.

3.03	INSTALLATION

A.	Install the work in accordance with manufacturer instructions.

3.04	WARRANTIES

A.	Two year limited warranty on all components.

3.05	CLEANING

A.	Leave the premises clean and free of residue of work of this section.

END OF SECTION