DIVISION 8

SECTION 08300

SPECIALTY DOOR SYSTEMS

PART 1 - GENERAL

1.01 SECTION INCLUDES

A.	Power operated Paired Swinging Stainless Steel U.L. Rated Fire Door System and accessories for complete installation.

1.02	RELATED SECTIONS

A.	Division 16 - Electrical

1.03	SUBMITTALS

A.	Product Data: Completely describing components.

- Shop Drawings: Showing details of fabrication, installation and accommodation to connecting work.

- Installation Instructions: For door, and accessories.

- Operating and Maintenance Data: For door, and accessories.

1.04	QUALITY ASSURANCE

A.	Installer Qualification: Door manufacturer, or trained, approved and licensed door installer.

PART 2 - PRODUCT

2.01 MANUFACTURERS

A.	Model 235SSF power operated Excel Paired Swinging Stainless Steel U.L. Rated Fire Door System as manufactured by ASI Doors, Inc., Milwaukee, WI.

B.	Substitutions:

No substitution will be considered unless written request for approval has been submitted by the bidder and has been received by the architect at least ten (10) days prior to the date for receipt of bids.

Each such request shall include the name of the materials for which it is to be substituted and a complete description of the proposed substitute, including drawings, cuts, mockups, performance and test data, a list of projects of similar scope and photographs of existing installations, and any other information necessary for evaluation.

2.02	PAIRED SWINGING STAINLESS STEEL U.L. RATED FIRE DOORS

A.	CLEANSEAL Model 235SSF power operated Excel Paired Swinging Stainless Steel U.L. Rated Fire Door System.

1.	Door size to fit door opening as shown on architectural drawings.

2.	Doors shall be 20, 45 or 90 minute, fire-rated powered pair of swing stainless steel doors.

3.	All door components to be constructed from 304, #4 brush stainless steel, including internal components, reinforcements, and anchorages.  All hardware reinforcements to be minimum 12 gauge stainless steel.

4.	Door panels shall be made of 16 gauge type 304 stainless steel.  Doors shall be polished to a #4 finish with the grain running vertically.  Finish to be covered by a protective plastic.  Doors shall have INVISIBLE EDGE SEAMS continuously welded, ground smooth, refinished, and repolished on all four sides and corners or panel.  Door bevel shall be 1/8" bevel on 2".

5.	Door shall have a U.L. rated honeycomb core completely filling the inside of the door and laminated to both face skins.

6.	Stainless steel door frames shall be 16 gauge 304, #4 finish with industry standard 2" face with variable profile.  Frames shall be continuously welded units.  Corner joints shall have all contact edges closed tight.  Faces to be mitered, welded, ground smooth and polished.

7.	Standard hardware to include:  stainless steel butt hinges, applied with stainless steel fasteners; and a positive latching device, constructed of stainless steel on exposed surfaces.  (Hardware to be manufacturers standard unless otherwise specified.)

8.	Power drive system to be electromechanically operated, 110 volt power open and spring close.  Operator works as a conventional manual door closer in event of power failure.  Actuation provided by low voltage pushplate or other options as specified.

9.	Swing side of door to be protected by a header mounted infrared motion sensor device.

10.	Gaskets at sides, head, astragal, and sill to be non-marking.

11.	Window kit option will include two 45 degree sloped stainless steel frames, sized up to 100 square inches for 90 minute rated.  24" x 24" vision available for 45 and 20 minute doors.

12.	90 minute Class B Rating - maximum door panel size is 4'0" x 7'2", 3/4" latch throw, 16 gauge, swinging as one panel.

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Verify installation conditions as satisfactory to receive work of this section. Do not install until unsatisfactory conditions are corrected. Beginning work constitutes your acceptance of conditions as satisfactory.

1.	Verify opening size, dimensions and tolerances.

3.02	PREPARATION

A.	Protect surrounding areas and surfaces to prevent damage during work of this section.

3.03	INSTALLATION

A.	Install the work in accordance with manufacturer instructions.

3.04	WARRANTIES

A.	One year limited warranty on all components.

3.05	CLEANING

A.	Leave the premises clean and free of residue of work of this section.

END OF SECTION